## About
Notes on this data set:
This data set provides inputs for a capacity expansion planning study considering options for a 100% carbon-free electricity system across the U.S. portion of the Western Interconnection (Western Electricity Coordinating Council or WECC).
Only carbon-free resources are included in the candidate generation/storage options. Existing renewable energy, hydropower, pumped hydro storage, and nuclear power capacity is included across all states, but carbon-emitting existing resources are not included in the data set. Natural gas plants with CCS at 100% capture rate are included in the new build options by default, but less costly plants with 90% capture rate are also provided as an alternative option (users must switch New_Build flag = 0
There are 6 regions (see accompanying map) and time series data provided for 16 representative weeks (with hourly chronological resolution within each week). Each representative period represents 1 or more other weeks throughout the time series. The number of hours represented by each 168 hour 7 day period is given by the Representative_Period_Weight input column in the Inputs_data.csv file. Representative weeks and weights are determined via K-means clustering to minimize error in wind, solar, hydropower and demand time series within each cluster as per Mallapragada et al. (2018), Impact of model resolution on scenario outcomes for electricity sector system expansion, Energy 163 (DOI: https://doi.org/10.1016/j.energy.2018.08.015) and always include the peak demand week.
We provide two sets of inputs with different demand levels: a reference electrification case and a high electrification case. Demand profiles are from the NREL 2018 Electrification Futures Study https://www.nrel.gov/docs/fy18osti/70485.pdf and are for weather year 2012.
Renewables data profiles are from Vibrant Clean Energy, 13-km continental United States data set and are for weather year 2012
Technology costs are from NREL Annual Technology Baseline 2019 edition.
Transmission transfer limits from EPA IPM model
All inputs generated by PowerGenome data platform, see https://github.com/gschivley/PowerGenome

## Generators_data
File: | Generators_data.csv
Column: | R_ID | Zone_name | Zone | Technology | Cluster | New_Build | Num_Units | Cap_size | Existing_Cap_MW | Existing_Cap_MWh | capex | Inv_cost_per_MWyr | capex_mwh | Inv_cost_per_MWhyr | Fixed_OM_cost_per_MWyr | Fixed_OM_cost_per_MWhyr | Var_OM_cost_per_MWh | Fuel | Heat_rate_MMBTU_per_MWh | heat_rate_mmbtu_mwh_iqr | heat_rate_mmbtu_mwh_std | Min_power | Ramp_Up_percentage | Ramp_Dn_percentage | Commit | Start_fuel_MMBTU_per_MW | Start_cost_per_MW | Up_time | Down_time | Charge_efficiency | Discharge_efficiency | Min_Duration | Max_Duration | THERM | VRE | MUSTRUN | STOR | HYDRO | RPS | CES
Description | Resource ID | Zone name | Zone ID | Technology name | Cluster ID (by tech and zone) | Flag indicating whether this resource is eligible for new build or retirement: -1 indicates existing resource ineligible for retirement (must continue operating); 0 indicates existing resource, eligible for retirement; 1 indicates new build resource; | Number of generating units in cluster | Capacity size per unit in cluster (= Existing_Cap_MW/Num_units) | Installed power capacity (MW) | Installed energy storage capacity (MWh; non-zero only for storage and reservoir hydro resources) | Total capital expenditure for new build resources ($/MW); not used by model, but basis for annuitized Inv_cost_per_MWyr and provided if you wish to recalculate with different WACC and asset life | Annuitized capacity investment cost (annual cost, $/MW-year) | Total capital expenditure for new build resources ($/MWh of storage capacity); not used by model, but basis for annuitized Inv_cost_per_MWyr and provided if you wish to recalculate with different WACC and asset life | Annuitized energy storage capacity investment cost (annual cost, $/MWh-year) | Fixed O&M cost (annual cost, $/MW-yr) | Fixed O&M cost for energy storage capacity (annual cost, $/MWh-yr) | Variable O&M cost (annual cost, $/MWh) | Fuel type (Must match one of the fuels in Fuels.csv input) | Heat rate (fuel consumption in MMBtu per MWh) | Cluster interquartile range for heat rate variation (metric to assess cluster error; not used in model) | Cluster standard deviation for heat rate variation (metric to assess cluster error; not used in model) | Minimum stable output power (as p.u. share of max capacity) | Maximum hourly ramp up (increase in power output) (as p.u. share of max capacity) | Maximum hourly ramp down (decrease in power output) (as p.u. share of max capacity) | Binary flag indicating membership in set of generators for which unit commitment constraints/decisions apply | Start-up fuel consumpion (MMBtu per start) | Start-up O&M cost ($ per start) | Minimum up time (hours after start-up unit must remain online) | Minimum down time (hours after shut-down unit must remain offline) | Storage charge efficiency (only for storage units in set STOR) | Storage charge efficiency (only for storage units in set STOR) | Minimum energy to power capacity ratio for new build energy storage | Maximum energy to power capacity ratio for new build energy storage | Binary flag indicating membership in thermal units set (to which min power and ramp rate constraints apply) | Binary flag indicating membership in variable renewable resource set | Binary flag indicating membership in set of must-run (constant output) resources | Binary flag indicating membership in energy storage set | Binary flag indicating membership in hydropower set (reservoir and run of river hydro) | Binary flag indicating eligibility for Renewable Portoflio Standard policies | Binary flag indicating eligibility for Clean Electricity Standard policies
Type | Int (unique) | String (unique) | Int (unique) | String | Int | Int from set {-1,0,1} | Int | Float | Float | Float | Float | Float | Float | Float | Float | Float | Float | String | Float | Float | Float | Float (0 to 1) | Float (0 to 1) | Float (0 to 1) | Binary (0,1) | Float | Float | Int | Int | Float (0 to 1) | Float (0 to 1) | Int | Int | Binary (0,1) | Binary (0,1) | Binary (0,1) | Binary (0,1) | Binary (0,1) | Binary (0,1) | Binary (0,1)

## Generators_variability
File: | Generators_variability.csv
Columns: | One column for each generator row in Generators_data.csv, in same order as the generators
Rows: | One row per time period (hours)
Entries: | Hourly capacity factor (maximum power production as p.u. share of maximum capacity)
Type: | Float

## Fuels_data
File: | Fuels_data.csv
Column: | Fuel | Cost_per_MMBtu | CO2_content_tons_per_MMBtu | fuel_indices
Description | Fuel type | Fuel cost ($ per MMBtu of fuel) | CO2 content of fuel (tons CO2 per MMBtu of fuel) | Fuel index
Type | String (unique) | Float | Float | Int (unique)

## Load_data
File: | Load_data.csv
Column: | Voll | Demand_segment | Cost_of_demand_curtailment_perMW | Max_demand_curtailment | Representative_Periods | Hours_per_period | Representative_Period_Index | Representative_Period_Weight | Time_index | Load_MW_zN
Description: | Value of lost load or opportunity cost (lost utility) of involuntary demand curtailment ($/MWh curtailed) | Voluntary demand curtailment (elastic demand) segment index | Cost of voluntary demand curtailement or opportunity cost/willingness to pay of elastic demand ($/MWh curtailed) | Maximum voluntary demand curtailment per segment (as p.u. share of hourly demand) | Number of representative time periods (for time domain reduction) | Number of hours per representative time period | Index of representative sample period (cluster) | Number of hours in the year represented by each sample period | Time period index (hour) | Next N rows are load (demand) per time period (hour) in each zone z in 1:Z (MWh per hour)
Type: | Int | Int (unique) | Float | Float | Int | Int | Int | Int | Int (unique) | Float

## Cluster_order
File: | Cluster_order.csv
Column: | Index | Cluster
Description: | Index of time period (each of same length as Hours_per_period in Load_data.csv) in chronological order through the year | Index of representative time period that represents this time period (matching indices in Representative_Period_Index in Load_data.csv)
Type: | Int | Int

## Network
File: | Network.csv
Column: | Transmission Path Name | Network_line | z1 | … | zN | Line_Max_Flow_MW | Distance_mile | Line_Loss | Line_Max_Reinforcement_MW | Line_Reinforcement_Cost_per_MW_yr
Description: | Name of transmission path (describing zones connected) | Transmission line/path index | Next N columns: one column per network zone z in Z; 1 indicates line begins in zone n, -1 indicates line terminates/ends in zone n, 0 indicates line is not connected to zone n |  |  | Maximum transmission flow between each zone along each line (MW) | Transmission path distance (miles) | Transmission losses (as p.u. share of hourly power flows) | Maximum transmission expansion (MW) | Annuitized transmission expansion cost (annual, $/MW-yr)
Type: | String | Int (unique) | Int from set {-1,0,1} |  |  | Int | Float | Float | Int | Int

## Zones
File: | Zones.csv
Column: | Region description | Network_zones
Description: | Name of region/zone | Zone index
Type: | String (unique) | String (unique)

## Flexible_load_data
File: | Flexible_load_data.csv |  |  | Input data for time-shiftable/schedulable/flexible loads
Column: | ID | Zone_name | Zone | Load_type | Max_Capacity_MW | Max_Delay_Hrs
Description | Resource ID | Zone name | Zone ID | Type of flexible load | Maximum instantaneous demand of all devices of this load type (used in combination with hourly avaiability factor in Flexible_load_availability.csv) to determine hourly flexible load in each time period (MW) | Maximum number of hours this load can be delayed before it must be satisfied (hours)
Type | Int (unique) | String (unique) | Int (unique) | String | Float | Int

## Flexible_load_availability
File: | Flexible_load_availability.csv
Columns: | One column for each flexible demand row in Flexible_demand_data.csv, in same order as the rows
Rows: | One row per time period (hours)
Entries: | Hourly avaialbility factor (maximum hourly load by type as p.u. share of maximum instanataneous demand reported in Flexible_load_data.csv)
Type: | Float